## Legend
Sprout 1.2 LVSS Skid - Test Configuration (Section 1.1.5)
How to use this workbook
1. Yellow cells are inputs. Replace the EXAMPLE rows on each tab with this skid's real data, and add rows as needed.
2. Every example value marked PLACEHOLDER (models, IPs, Modbus addresses, raw ranges, limits) must be confirmed against the approved submittals and the MOXA / switch manuals.
3. Header row stays in row 1 of each table tab. Column names must not be changed; the tool reads them by name.
4. Start a row with # in column A to have the tool ignore it.
5. Hover over a column header to see what it means.
6. After editing, run: python run_tests.py check-config
Tabs
Skid_Info - project and skid identification printed on the report
Settings - tolerances, limits and timing used by the tests
IO_Modules - each MOXA ioLogik module
IO_Points - every IO channel (DI/DO/AI/AO) with its Modbus address and scaling
Network_Devices - every IP device to ping (PLC, HMI, meters, IO modules)
Switches / Switch_Ports - Juniper EX4100-H switches, expected port status and VLANs (ports by Junos name, e.g. ge-0/0/0)
Redundant_Links - ring / redundant links to pull during the failover test
SPDs - surge protective devices and their alarm contact tag
SCADA_Points - points to verify end-to-end on the SCADA screen (IO tag, or DEVICE.POINT for a PQM / breaker value)
Modbus_Devices - PQMs and breakers on the network (read and verify only; the tool never writes to them)
Device_Points - register definitions from each manufacturer's Modbus map, per device type or device
Device_Expected - expected settings per device (e.g. PT/CT ratios for PQM1), compared in test 1.1.5-2.8
PM8000 registers on Device_Points come from Schneider's PM8000_Modbus_Map.xlsx (Release 1 FW). Each address is the map's register number minus 1; the map number is shown in the description.
Device_Expected: enter each PQM's volts mode and PT/CT ratios from the drawings. Blank expected values are read and recorded in the report but not judged.

## Skid_Info
Field | Value | Notes
Project | EXAMPLE - Project name
Skid Model | Sprout 1.2 LVSS Skid
Skid Serial | EXAMPLE-SN-0001 | Used to name results folders and the report
Owner | EXAMPLE - Owner name
Site | EXAMPLE - Site
Test Plan Rev | EXAMPLE - Rev X | Revision of the Sprout 1.2 LVSS Skid Test Plan used
Approved Submittal Ref | EXAMPLE - Submittal no. | Reference for channel/config comparison
CxA | EXAMPLE - Commissioning agent

## Settings
Field | Value | Notes
modbus_port | 502 | Modbus TCP port on the ioLogik modules
modbus_timeout_s | 1 | Timeout per Modbus request
poll_interval_s | 1 | 1.1.5-1.6 polling interval
poll_duration_s | 600 | 1.1.5-1.6 polling test length (s). PLACEHOLDER - agree with CxA
poll_max_failures | 0 | Failed reads allowed per module (0 = no packet loss)
di_timeout_s | 30 | How long to wait for a DI to change after the prompt
ai_samples | 10 | Samples averaged at each analog test point
ai_sample_interval_s | 0.1
ai_test_points_pct | 0,25,50,75,100 | Default analog test points (% of span)
ai_tolerance_pct_span | 0.5 | Allowed AI error, % of span. PLACEHOLDER - use spec value
ai_noise_limit_pct_span | 0.25 | Allowed peak-to-peak spread of samples, % of span (signal distortion). PLACEHOLDER
ao_tolerance_pct_span | 0.5 | Allowed AO error, % of signal span. PLACEHOLDER
alarm_watch_s | 300 | 1.1.5-1.7 alarm logging window (s); Ctrl+C ends early
ping_count | 100 | Pings per device
ping_max_loss_pct | 0 | Allowed packet loss %
ping_max_avg_ms | 10 | Allowed average round trip (ms). PLACEHOLDER
snmp_community | public | Default read community (per-switch value on Switches tab overrides)
snmp_port | 161
snmp_timeout_s | 2
failover_sample_ms | 20 | Heartbeat read interval during failover test (E1210 read)
failover_baseline_s | 5 | Healthy baseline before the link is pulled
failover_window_s | 15 | Time allowed to pull / restore the link
failover_max_ms | 1000 | Default failover limit (ms). PLACEHOLDER - depends on protocol (ERPS is designed for <=50 ms; RSTP varies). Use the spec value agreed with the CxA
continuity_max_ohm | 1 | Max continuity reading for SPD circuit. PLACEHOLDER - use spec value
spd_alarm_timeout_s | 60 | Wait for SPD aux contact to change
device_poll_s | 60 | 1.1.5-2.7 PQM / breaker polling test length (s)
device_poll_interval_s | 1 | 1.1.5-2.7 polling interval
device_poll_max_failures | 0 | Failed reads allowed per device
device_meas_tol_pct | 1 | 1.1.5-2.9 default allowed error vs reference, % of reading. PLACEHOLDER - agree with CxA

## IO_Modules
module_id | model | ip | unit_id | firmware_expected | location | notes
IO-01 | ioLogik E1210 | 192.168.127.101 | 1 |  | LVSS control section | 16 DI, Modbus FC02 DI_status addresses 0-15 = DI-00 to DI-15
Note on A1: Short ID used on other tabs, e.g. IO-01
Note on B1: ioLogik model
Note on D1: Modbus unit ID (usually 1)
Note on E1: Firmware per approved submittal

## IO_Points
tag | description | module_id | point_type | channel | modbus_table | address | signal_range | raw_min | raw_max | eng_min | eng_max | eng_units | test_points_pct | is_alarm | normal_state | contact_type | expected_config | notes
AUTO_MODE | DI0 - AUTO MODE | IO-01 | DI | 0 | discrete_input | 0 | [7 empty] | N |  | NO | DI mode | Status. Opposite of MANUAL_MODE
MANUAL_MODE | DI1 - MANUAL MODE | IO-01 | DI | 1 | discrete_input | 1 | [7 empty] | N |  | NO | DI mode | Status. Opposite of AUTO_MODE
MAIN_A_PREF_SOURCE | DI2 - MAIN-A PREF. SOURCE | IO-01 | DI | 2 | discrete_input | 2 | [7 empty] | N |  | NO | DI mode | Status. Opposite of MAIN_B_PREF_SOURCE
MAIN_B_PREF_SOURCE | DI3 - MAIN-B PREF. SOURCE | IO-01 | DI | 3 | discrete_input | 3 | [7 empty] | N |  | NO | DI mode | Status. Opposite of MAIN_A_PREF_SOURCE
125VDC_S2_FAIL | DI4 - 125VDC S2 FAIL | IO-01 | DI | 4 | discrete_input | 4 | [7 empty] | Y | 0 | NO | DI mode
125VDC_S1_FAIL | DI5 - 125VDC S1 FAIL | IO-01 | DI | 5 | discrete_input | 5 | [7 empty] | Y | 0 | NO | DI mode
240VAC_S_FAIL | DI6 - 240VAC S FAIL | IO-01 | DI | 6 | discrete_input | 6 | [7 empty] | Y | 1 | NC | DI mode
SPD_ALARM | DI7 - SPD | IO-01 | DI | 7 | discrete_input | 7 | [7 empty] | Y | 1 | NC | DI mode | SPD dry aux alarm contact (test 1.1.5-3.4)
XFMR1_ALARM | DI8 - XFMR1 ALARM | IO-01 | DI | 8 | discrete_input | 8 | [7 empty] | Y | 0 | NO | DI mode
XFMR2_ALARM | DI9 - XFMR2 ALARM | IO-01 | DI | 9 | discrete_input | 9 | [7 empty] | Y | 0 | NO | DI mode
MAIN_A_LOCKOUT | DI10 - MAIN A LOCKOUT | IO-01 | DI | 10 | discrete_input | 10 | [7 empty] | Y | 1 | NC | DI mode
MAIN_B_LOCKOUT | DI11 - MAIN B LOCKOUT | IO-01 | DI | 11 | discrete_input | 11 | [7 empty] | Y | 1 | NC | DI mode
MAIN_A_ERMS_ON | DI12 - MAIN A ERMS ON | IO-01 | DI | 12 | discrete_input | 12 | [7 empty] | Y | 1 | NC | DI mode | Maintenance mode indication
MAIN_B_ERMS_ON | DI13 - MAIN B ERMS ON | IO-01 | DI | 13 | discrete_input | 13 | [7 empty] | Y | 1 | NC | DI mode | Maintenance mode indication
ATC_READY | DI14 - ATC READY FOR OPERATION | IO-01 | DI | 14 | discrete_input | 14 | [7 empty] | N |  | NO | DI mode | Status
SPARE_DI15 | DI15 - SPARE | IO-01 | DI | 15 | discrete_input | 15 | [7 empty] | N |  |  | DI mode | Spare
Note on A1: Unique tag name
Note on C1: From IO_Modules
Note on D1: DI, DO, AI or AO
Note on E1: Channel number on the module
Note on F1: discrete_input, coil, input_register or holding_register
Note on G1: Modbus address (0-based) from the ioLogik manual. PLACEHOLDER until confirmed
Note on H1: AI/AO only, e.g. 4-20mA or 0-10V
Note on I1: AI/AO raw register value at bottom of signal range. PLACEHOLDER - confirm in ioLogik manual
Note on J1: AI/AO raw register value at top of signal range
Note on K1: Engineering value at bottom of range
Note on N1: Optional, overrides Settings, e.g. 0,50,100
Note on O1: Y if this DI is an alarm point for 1.1.5-1.7
Note on P1: DI value in normal (healthy) operation: 1 = contact closed, 0 = open. Required for alarm points
Note on Q1: NO or NC in normal operation, as given by engineering (NO = open = 0, NC = closed = 1)
Note on R1: Channel settings to verify in ioAdmin (mode, filter, etc.)

## Network_Devices
device_name | ip | device_type | vlan | switch_id | switch_port | ping_required
IO-01 | 192.168.127.101 | MOXA ioLogik E1210 | 10 | SW-01 | ge-0/0/0 | Y
PLC-01 | 192.168.127.10 | PLC / RTU (PLACEHOLDER) | 10 | SW-01 | ge-0/0/1 | Y
HMI-01 | 192.168.127.50 | HMI (PLACEHOLDER) | 10 | SW-02 | ge-0/0/0 | Y
Note on G1: Y/N, default Y

## Switches
switch_id | model | platform | ip | snmp_community | ssh_user | approved_config_file | redundancy_protocol | firmware_expected | location
SW-01 | EX4100-H-12MP (PLACEHOLDER - confirm 12MP or 24MP) | junos | 192.168.127.253 |  | testuser | approved/SW-01.set | RSTP (PLACEHOLDER) |  | LVSS comm section
SW-02 | EX4100-H-12MP (PLACEHOLDER) | junos | 192.168.127.254 |  | testuser | approved/SW-02.set | RSTP (PLACEHOLDER) |  | LVSS comm section
Note on C1: junos for Juniper (VLAN + config read over SSH); blank = SNMP only
Note on D1: Management IP
Note on E1: Leave blank to use Settings value. SNMP v2c read-only must be enabled on the switch
Note on F1: Junos login (not root). Password is asked for at run time and never stored
Note on G1: Approved config in 'display set' format, path relative to this config folder
Note on H1: RSTP, MSTP or ERPS per network design
Note on I1: Junos version, e.g. 23.4R2-S3

## Switch_Ports
switch_id | port | if_index | bridge_port | description | expected_status | expected_speed_mbps | pvid | tagged_vlans | untagged_vlans
SW-01 | ge-0/0/0 |  |  | IO-01 | up | 100 | 10 |  | 10
SW-01 | ge-0/0/1 |  |  | PLC-01 | up | 1000 | 10 |  | 10
SW-01 | ge-0/0/7 |  |  | Unused | disabled
SW-01 | xe-0/2/0 |  |  | Uplink to SW-02 | up | 10000 | 1 | 10,20 | 1
Note on B1: Junos interface name, e.g. ge-0/0/0 or mge-0/0/0 (as in 'show interfaces terse')
Note on C1: Optional. Blank = looked up from the interface name
Note on D1: Non-Juniper switches only (Q-BRIDGE port no.)
Note on F1: up, down or disabled
Note on G1: Checked only when up
Note on H1: Native / port VLAN ID
Note on I1: e.g. 10,20 or 30-32; blank = not checked

## Redundant_Links
link_id | description | switch_a | port_a | switch_b | port_b | monitor_tag | max_failover_ms
RL-01 | Redundant uplink SW-01 to SW-02 | SW-01 | xe-0/2/0 | SW-02 | xe-0/2/0 | AUTO_MODE
Note on G1: IO point read continuously during the test (must be reachable across the link)
Note on H1: Blank = Settings value

## SPDs
spd_id | location | manufacturer | model | type | max_lead_length_in | alarm_tag | fault_sim_method | notes
SPD-01 | LVSS main bus | PLACEHOLDER | PLACEHOLDER | Type 2 | 12 | SPD_ALARM | Remove replaceable module per mfr. instructions
Note on E1: Type 1 / Type 2 etc.
Note on F1: Per manufacturer instructions / spec. PLACEHOLDER
Note on G1: DI tag the aux contact is wired to; blank = verify with meter
Note on H1: How to simulate a fault safely

## SCADA_Points
tag | scada_name | test_method | expected_update_s
AUTO_MODE | AUTO MODE | Operate device or jumper input at terminal | 2
MANUAL_MODE | MANUAL MODE | Operate device or jumper input at terminal | 2
MAIN_A_PREF_SOURCE | MAIN-A PREF. SOURCE | Operate device or jumper input at terminal | 2
MAIN_B_PREF_SOURCE | MAIN-B PREF. SOURCE | Operate device or jumper input at terminal | 2
125VDC_S2_FAIL | 125VDC S2 FAIL | Operate device or jumper input at terminal | 2
125VDC_S1_FAIL | 125VDC S1 FAIL | Operate device or jumper input at terminal | 2
240VAC_S_FAIL | 240VAC S FAIL | Operate device or jumper input at terminal | 2
SPD_ALARM | SPD | Simulate SPD fault | 2
XFMR1_ALARM | XFMR1 ALARM | Operate device or jumper input at terminal | 2
XFMR2_ALARM | XFMR2 ALARM | Operate device or jumper input at terminal | 2
MAIN_A_LOCKOUT | MAIN A LOCKOUT | Operate device or jumper input at terminal | 2
MAIN_B_LOCKOUT | MAIN B LOCKOUT | Operate device or jumper input at terminal | 2
MAIN_A_ERMS_ON | MAIN A ERMS ON | Operate device or jumper input at terminal | 2
MAIN_B_ERMS_ON | MAIN B ERMS ON | Operate device or jumper input at terminal | 2
ATC_READY | ATC READY FOR OPERATION | Operate device or jumper input at terminal | 2
PQM1.V_AB | PQM1 VOLTAGE A-B (PLACEHOLDER name) | Compare with PQM front display | 2
PQM2.V_AB | PQM2 VOLTAGE A-B (PLACEHOLDER name) | Compare with PQM front display | 2
PQM3.V_AB | PQM3 VOLTAGE A-B (PLACEHOLDER name) | Compare with PQM front display | 2
#MAIN-A.CB_STATE | MAIN-A BREAKER STATUS | Enable once CB_STATE register is filled in | 2
#AUTOXFMR.CB_STATE | AUTOXFMR BREAKER STATUS |  | 2
#ACC-UPS.CB_STATE | ACC-UPS BREAKER STATUS |  | 2
#MAIN-B.CB_STATE | MAIN-B BREAKER STATUS |  | 2
Note on A1: Field tag from IO_Points
Note on B1: Point name on the SCADA screen
Note on D1: Max time for the change to appear on SCADA

## Modbus_Devices
device_id | device_type | model | ip | port | unit_id | word_order | timeout_s | switch_id | switch_port | location
PQM1 | PM8000 | Schneider PowerLogic PM8000 | 192.168.127.111 |  | 1 | big |  | SW-01 |  | PLACEHOLDER
PQM2 | PM8000 | Schneider PowerLogic PM8000 | 192.168.127.112 |  | 1 | big |  | SW-01 |  | PLACEHOLDER
PQM3 | PM8000 | Schneider PowerLogic PM8000 | 192.168.127.113 |  | 1 | big |  | SW-01 |  | PLACEHOLDER
MAIN-A | ABB_EKIP | ABB breaker, Ekip Com Modbus TCP (PLACEHOLDER - frame/trip unit) | 192.168.127.121 |  | 1 | big |  | SW-01
AUTOXFMR | ABB_EKIP | ABB breaker, Ekip Com Modbus TCP (PLACEHOLDER) | 192.168.127.122 |  | 1 | big |  | SW-01
ACC-UPS | ABB_EKIP | ABB breaker, Ekip Com Modbus TCP (PLACEHOLDER) | 192.168.127.123 |  | 1 | big |  | SW-01
MAIN-B | ABB_EKIP | ABB breaker, Ekip Com Modbus TCP (PLACEHOLDER) | 192.168.127.124 |  | 1 | big |  | SW-02
Note on A1: Name used in reports and SCADA tags, e.g. PQM1
Note on B1: Links to Device_Points, e.g. PM8000 or ABB_EKIP
Note on E1: Blank = 502
Note on F1: Modbus unit ID. PLACEHOLDER - confirm on each device
Note on G1: big = high word first (Schneider). Check ABB System Interface doc
Note on H1: Blank = Settings value

## Device_Points
applies_to | point | category | description | function | address | data_type | bit | scale | units | state_map | expected_default | tolerance | tolerance_pct | sim_value | registers
PM8000 | METER_NAME | identity | Meter name (map 30). Set to PQM1/2/3 in ION Setup to catch IP mix-ups | holding_register | 29 | utf8 | [8 empty] | 20
PM8000 | METER_MODEL | identity | Meter model (map 50) | holding_register | 49 | utf8 | [8 empty] | 20
PM8000 | FIRMWARE | identity | Firmware version (map 1717). Expected 004.007.001 on all PQMs | holding_register | 1716 | utf8 |  |  |  |  | 004.007.001 |  |  |  | 6
PM8000 | VOLTS_MODE | setting | Volts mode (map 54001) | holding_register | 54000 | uint16 |  |  |  | 0=4W-WYE;1=DELTA;2=SINGLE;3=DEMO;4=3W-WYE
PM8000 | PT_PRIMARY | setting | PT primary (map 56001) | holding_register | 56000 | int32 |  |  | V
PM8000 | PT_SECONDARY | setting | PT secondary (map 56003) | holding_register | 56002 | int32 |  |  | V
PM8000 | CT_PRIMARY | setting | CT primary (map 56005) | holding_register | 56004 | int32 |  |  | A
PM8000 | CT_SECONDARY | setting | CT secondary (map 56007) | holding_register | 56006 | int32 |  |  | A
PM8000 | I4_CT_PRIMARY | setting | I4 (neutral) CT primary (map 56009). Recorded only | holding_register | 56008 | int32 |  |  | A
PM8000 | I4_CT_SECONDARY | setting | I4 (neutral) CT secondary (map 56011). Recorded only | holding_register | 56010 | int32 |  |  | A
PM8000 | FREQ_NOMINAL | setting | Nominal frequency (map 54396) | holding_register | 54395 | uint16 |  |  |  | 0=60Hz;1=50Hz | 60Hz
PM8000 | I1_POLARITY | setting | CT polarity phase A (map 54002) | holding_register | 54001 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | I2_POLARITY | setting | CT polarity phase B (map 54003) | holding_register | 54002 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | I3_POLARITY | setting | CT polarity phase C (map 54004) | holding_register | 54003 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | V1_POLARITY | setting | PT polarity V1 (map 54587) | holding_register | 54586 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | V2_POLARITY | setting | PT polarity V2 (map 54588) | holding_register | 54587 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | V3_POLARITY | setting | PT polarity V3 (map 54589) | holding_register | 54588 | uint16 |  |  |  | 0=Normal;1=Inverted | Normal
PM8000 | COM1_UNIT_ID | identity | RS-485 (COM1) unit ID (map 56979). Recorded only; not the Ethernet unit ID | holding_register | 56978 | int32
PM8000 | I_A | measurement | Current A (map 3000) | holding_register | 2999 | float32 |  |  | A |  |  |  |  | 100
PM8000 | I_B | measurement | Current B (map 3002) | holding_register | 3001 | float32 |  |  | A |  |  |  |  | 100
PM8000 | I_C | measurement | Current C (map 3004) | holding_register | 3003 | float32 |  |  | A |  |  |  |  | 100
PM8000 | V_AB | measurement | Voltage A-B (map 3020) | holding_register | 3019 | float32 |  |  | V |  |  |  |  | 480
PM8000 | V_BC | measurement | Voltage B-C (map 3022) | holding_register | 3021 | float32 |  |  | V |  |  |  |  | 480
PM8000 | V_CA | measurement | Voltage C-A (map 3024) | holding_register | 3023 | float32 |  |  | V |  |  |  |  | 480
PM8000 | KW_TOTAL | measurement | Active power total (map 3060, in W; scaled to kW) | holding_register | 3059 | float32 |  | 0.001 | kW |  |  |  | 2 | 70
PM8000 | PF_TOTAL | measurement | Power factor total, signed (map 3150). Enter the reference with the same sign | holding_register | 3149 | float32 | [6 empty] | 2 | 0.95
PM8000 | FREQ | measurement | Frequency (map 3110) | holding_register | 3109 | float32 |  |  | Hz |  |  |  | 0.1 | 60
#ABB_EKIP | CB_STATE | status | Breaker open/closed - address and bit from ABB System Interface doc | holding_register |  | uint16 |  |  |  | 0=Open;1=Closed
#ABB_EKIP | CB_TRIPPED | status | Breaker tripped | holding_register |  | uint16 |  |  |  | 0=Not tripped;1=Tripped
#ABB_EKIP | CB_POSITION | status | Racked in / out (withdrawable only) | holding_register |  | uint16 |  |  |  | 0=Racked out;1=Racked in
#ABB_EKIP | EKIP_REMOTE | setting | Local/Remote mode (confirm expected with owner) | holding_register |  | uint16 |  |  |  | 0=Local;1=Remote
Note on A1: A device_type (all devices of that type) or one device_id. Start with # to disable a row
Note on B1: Short name, used in Device_Expected and SCADA tags
Note on C1: identity, setting, measurement or status
Note on E1: holding_register (FC03) or input_register (FC04)
Note on F1: 0-based register address from the manufacturer's map (register number minus 1 if the map is 1-based)
Note on G1: uint16, int16, uint32, int32, float32, uint64, int64, float64
Note on H1: Optional: bit number within the value, for status bits
Note on I1: Optional multiplier, e.g. 0.1
Note on K1: For status / enumerated settings, e.g. 0=Open;1=Closed
Note on L1: Expected value for every device of this type (Device_Expected overrides)
Note on M1: Allowed difference for numeric settings
Note on N1: Measurements: allowed error % of reading (blank = Settings value)
Note on O1: Value used in simulation only
Note on P1: utf8 text points only: the map's '# of Modbus Registers'

## Device_Expected
device_id | point | expected | tolerance | notes
PQM1 | METER_NAME |  |  | Optional: set the meter name in ION Setup, then enter it here
PQM1 | VOLTS_MODE |  |  | Enter from drawings: 4W-WYE, DELTA, 3W-WYE or SINGLE
PQM1 | PT_PRIMARY |  |  | Enter from drawings (V)
PQM1 | PT_SECONDARY |  |  | Enter from drawings (V)
PQM1 | CT_PRIMARY |  |  | Enter from drawings (A)
PQM1 | CT_SECONDARY |  |  | Enter from drawings (A)
PQM2 | METER_NAME |  |  | Optional: set the meter name in ION Setup, then enter it here
PQM2 | VOLTS_MODE |  |  | Enter from drawings: 4W-WYE, DELTA, 3W-WYE or SINGLE
PQM2 | PT_PRIMARY |  |  | Enter from drawings (V)
PQM2 | PT_SECONDARY |  |  | Enter from drawings (V)
PQM2 | CT_PRIMARY |  |  | Enter from drawings (A)
PQM2 | CT_SECONDARY |  |  | Enter from drawings (A)
PQM3 | METER_NAME |  |  | Optional: set the meter name in ION Setup, then enter it here
PQM3 | VOLTS_MODE |  |  | Enter from drawings: 4W-WYE, DELTA, 3W-WYE or SINGLE
PQM3 | PT_PRIMARY |  |  | Enter from drawings (V)
PQM3 | PT_SECONDARY |  |  | Enter from drawings (V)
PQM3 | CT_PRIMARY |  |  | Enter from drawings (A)
PQM3 | CT_SECONDARY |  |  | Enter from drawings (A)
Note on A1: From Modbus_Devices. Start with # to disable a row
Note on B1: From Device_Points
Note on C1: Expected value; for state points use the state name
Note on D1: Optional, overrides Device_Points